[image: image1.jpg]Keyes



Life Safety Documentation Requirements
Revision:10 7/14/18

Based on the 2012 edition of the Life Safety Code, for all Healthcare facilities
Date Assessment: __________________________

Facility Name: ______________________________________ Location: __________________________________________________

	
	
	
	
	
	
	Date of
	Compliant?
	

	Fire Alarm Test Report
	Devices/Function
	Frequency
	NFPA Standard
	Most Recent
	Yes
	No    N/A
	Comment

	
	
	Waterflow switches
	Semi-annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Smoke detectors
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	Initiating Devices
	Heat detectors
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Duct detectors
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Manual pull stations
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Low air pressure switches
	Quarterly
	72-2010; 14.4.5
	
	
	
	
	
	

	Supervisory Signal Devices
	Low water level switches
	Quarterly
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Tamper switches
	Semi-annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Strobes
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	Notification Devices
	Horns
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	Bells
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	Chimes
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Magnetic hold-open
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Air handler shut-down
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Kitchen hood suppression sys
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Elevator recall
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	Interface relays and modules
	Magnetic locks / Electric strikes
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	Fire pump
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	Smoke dampers
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	CO2/Clean agent suppression
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Sprinkler dry-pipe/pre-action
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Overhead rolling fire doors
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Charger test
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	Control panel batteries
	Discharge test
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	
	
	Load voltage test
	Semi-annually
	72-2010; 14.4.5
	
	
	
	
	
	

	Smoke detector sensitivity test
	
	2-Years*
	72-2010; 14.4.5
	
	
	
	
	
	

	Off-premises monitoring transmission equipment
	Annually
	72-2010; 14.4.5
	
	
	
	
	
	

	Fire Suppression System Test Report
	
	
	
	
	
	
	
	

	Portable fire extinguishers
	
	Inspection
	Monthly
	10-2010; 7.2.1.2
	
	
	
	
	
	

	
	
	Maintenance
	Annually
	10-2010; 7.3.1.1.1
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	Kitchen hood system – inspection
	Monthly
	17A-2009; 7.2.1
	
	
	
	
	
	

	
	
	Kitchen hood system – test
	Semi-annually
	17A-2009; 7.3.3
	
	
	
	
	
	

	
	
	Halon system – inspection & test
	Semi-annually
	12A-2009; 6.1.1
	
	
	
	
	
	

	Alternative suppression
	
	CO2 system – inspection
	Monthly
	12-2011 4.8.1
	
	
	
	
	
	

	systems
	
	CO2 system – tank weigh
	Semi-annually
	12-2011; 4.8.3.5.1
	
	
	
	
	
	

	
	
	CO2 system – test
	Annually
	12-2011; 4.8.3.2
	
	
	
	
	
	

	
	
	Clean agent system – inspection
	Semi-annually
	2001-2012; 7.1.3
	
	
	
	
	
	

	
	
	Clean agent system – test
	Annually
	2001-2012; 7.1.1
	
	
	
	
	
	


	
	
	
	
	
	
	Date of
	Compliant?
	
	

	Fire Suppression (cont’d) Devices/Function
	Frequency
	NFPA Standard
	Most Recent
	Yes
	No
	N/A
	Comment

	
	Fire pump churn test
	Monthly
	25-2011; 8.3.1
	
	
	
	
	
	
	
	

	
	Control valve inspection
	Monthly
	25-2011; 13.3.2.1.1
	
	
	
	
	
	
	
	

	
	Pressure Gauge Inspection
	Monthly
	25-2011; 13.2.7.1
	
	
	
	
	
	
	
	

	
	Fire department connections
	Quarterly
	25-2011; 13.7.1
	
	
	
	
	
	
	
	

	
	Fire hose valve – Inspection
	Quarterly
	25-2011; 13.5.6.1
	
	
	
	
	
	
	
	

	
	Pre-action/Dry pipe valve priming
	Quarterly
	25-2011; 13.4.3.2.1
	
	
	
	
	
	
	
	

	
	water test
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	Sprinkler inspection
	Annually
	25-2011; 5.2.1
	
	
	
	
	
	
	
	

	
	Piping & hanger inspection
	Annually
	25-2011; 5.2.2
	
	
	
	
	
	
	
	

	
	Pre-action/Dry pipe valve trip test
	Annually
	25-2011; 13.4.3.2.2
	
	
	
	
	
	
	
	

	
	Main drain test
	Quarterly*
	25-2011; 13.2.5.1
	
	
	
	
	
	
	
	

	
	
	Annually
	25-2011; 13.2.5
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	Control valve exercise
	Annually
	25-2011; 13.3.3.1
	
	
	
	
	
	
	
	

	
	Backflow preventer
	Annually
	25-2011; 13.6.2
	
	
	
	
	
	
	
	

	Water-based suppression
	Anti-freeze test
	Annually
	25-2011; 5.3.4
	
	
	
	
	
	
	
	

	systems
	Private service fire hydrants
	Annually
	25-2011; 7.3.2
	
	
	
	
	
	
	
	

	
	2½ inch fire hose valve – test
	Annually
	25-2011; 13.5.6.2.1
	
	
	
	
	
	
	
	

	
	Fire pump flow test
	Annually
	25-2011; 8.3.3
	
	
	
	
	
	
	
	

	
	Occupant use fire hose – inspect
	Annually
	1962-2008; 4.3.4
	
	
	
	
	
	
	
	

	
	1½ inch fire hose valve - test
	3-Years
	25-2011; 13.5.6.2.2
	
	
	
	
	
	
	
	

	
	Occupant use fire hose – pressure
	5-Years, then
	1962-2008; 4.3.2
	
	
	
	
	
	
	
	

	
	test
	every 3-Years
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	Check valve inspection
	5-Years
	25-2011; 13.4.2.1
	
	
	
	
	
	
	
	

	
	Pressure gauge calibration
	5-Years
	25-2011; 5.3.2
	
	
	
	
	
	
	
	

	
	Standpipe waterflow test
	5-Years
	25-2011; 6.3.1
	
	
	
	
	
	
	
	

	
	Private fire service mains
	5-Years
	25-2011; 7.3.1
	
	
	
	
	
	
	
	

	
	Internal inspection of piping
	5-Years
	25-2011; 14.2.1
	
	
	
	
	
	
	
	

	
	Dry Head sprinkler replacement
	10-Years
	25-2011; 5.3.1.1.1.6
	
	
	
	
	
	
	
	

	
	QR sprinkler head replacement
	20-Years
	25-2011; 5.3.1.1.1.3
	
	
	
	
	
	
	
	

	
	SR sprinkler head replacement
	50-Years
	25-2011; 5.3.1.1.1
	
	
	
	
	
	
	
	

	
	Spare Sprinkler List
	One-Time
	13-2010; 6.2.9.7
	
	
	
	
	
	
	
	

	Additional Testing & Inspection Requirements
	
	
	
	
	
	
	
	
	
	

	
	Inspection
	Weekly
	110-2010; 8.4.1
	
	
	
	
	
	
	
	

	
	Battery electrolyte levels / Voltage
	Monthly
	110-2010; 8.3.7.1
	
	
	
	
	
	
	
	

	
	Monthly load test
	20 days to 40
	110-2010; 8.4.2 and
	
	
	
	
	
	
	
	

	
	
	days
	99-2012; 6.4.4.1.1.4
	
	
	
	
	
	
	
	

	Emergency power generators
	
	
	
	
	
	
	
	
	
	
	

	
	Annual load test (if required)
	Annually*
	110-2010; 8.4.2.3
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	Annual Fuel Test
	Annually
	110-2010; 8.3.8
	
	
	
	
	
	
	
	

	
	Replace lead-acid start batteries
	24-30 Months
	110-2010, A.5.6.4.5.1
	
	
	
	
	
	
	
	

	
	3-Year 4-Hour load test
	3-Years
	110-2010; 8.4.9
	
	
	
	
	
	
	
	

	
	Inspection of ATS
	Weekly
	110-2010; 8.4.1
	
	
	
	
	
	
	
	

	Automatic Transfer Switches
	Monthly test with generator
	20 days to 40
	110-2010; 8.4.6 and
	
	
	
	
	
	
	
	

	
	
	days
	99-2012; 6.4.4.1.1.4
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	Maintenance & testing
	As per policy
	99-2012; 5.1.14.4.5
	
	
	
	
	
	
	
	

	
	Cross-contamination test
	After breach
	99-2012; 5.1.12.1.1
	
	
	
	
	
	
	
	

	Medical gas and Vacuum sys
	Purity and pressure test
	After breach
	99-2012; 5.1.12.1.1
	
	
	
	
	
	
	
	

	
	Non-stationary booms w/flexible
	18-months
	99-2012; 5.1.14.2.3.2
	
	
	
	
	
	
	
	

	
	connectors leak tested
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	



	
	
	
	
	
	
	Date of
	Compliant?
	
	

	
	Devices/Function
	Frequency
	NFPA Standard
	Most Recent
	Yes
	No
	N/A
	Comment

	
	Policy
	
	Review policy
	101-2012; 4.6.10.1
	
	
	
	
	
	
	

	Alternative Life Safety
	Implementation
	
	As needed per
	101-2012; 4.6.10.1
	
	
	
	
	
	
	

	
	
	
	policy
	
	
	
	
	
	
	
	

	Measures
	
	
	
	
	
	
	
	
	
	
	

	
	Fire Watch
	
	Continuous
	101-2012; 9.6.1.6 &
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	25-2011; 15.5.2
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	
	Inside hospital facility
	1-Year then 6-
	80-2010; 19.4 and
	
	
	
	
	
	
	

	
	
	years
	105-2010; 6.5.2
	
	
	
	
	
	
	

	Fire/Smoke damper test
	
	
	
	
	
	
	
	
	
	
	

	
	Outside hospital facility
	1-Year then 4-
	80-2010; 19.4 and
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	
	
	years
	105-2010; 6.5.2
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	Overhead rolling fire doors
	Drop test
	
	Annually
	80-2010; 5.2.1
	
	
	
	
	
	
	

	Side-hinged fire doors
	Annual test/inspection
	Annually
	101-2012; 8.3.3.1
	
	
	
	
	
	
	

	‘Exit’ signs
	Illumination inspection
	Monthly
	101-2012; 7.10.9.1
	
	
	
	
	
	
	

	Elevator recall
	Test of all elevators equipped with
	Monthly
	101-2012; 9.4.6.2
	
	
	
	
	
	
	

	
	Fire Fighter Service
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	Kitchen hood cleaning
	Remove grease
	
	Semi-annually
	96- 2011; 11.4
	
	
	
	
	
	
	

	Assessment of building
	Risk assessment to determine
	Annually
	99-2012; 4.2
	
	
	
	
	
	
	

	systems for Risk Category
	Category designation of systems
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	Ground Fault Circuit Interrupter
	Monthly test per manufacturer
	Monthly
	CMS §482.41(c)(2)
	
	
	
	
	
	
	

	Emergency Shower
	Flow test –
	ANSI Z358.1-2014
	Weekly
	4.6.3
	
	
	
	
	
	
	

	
	Inspection –
	ANSI Z358.1-2014
	Annually
	4.6.5
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	Emergency Eyewash
	Flow test –
	ANSI Z358.1-2014
	Weekly
	5.5.2
	
	
	
	
	
	
	

	
	Inspection –
	ANSI Z358.1-2014
	Annually
	5.5.5
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	

	Battery Powered
	Monthly test
	
	Monthly
	101-7.9.3.1.1 (1)
	
	
	
	
	
	
	

	Emergency Light
	Annual test
	
	Annually
	101-7.9.3.1.1 (3)
	
	
	
	
	
	
	

	Fire Drills – Healthcare
	1 per shift per quarter
	Quarterly
	101-19.7.1.6
	
	
	
	
	
	
	

	Fire Drills – Ambulatory
	1 per shift per quarter
	Quarterly
	101-21.7.1.6
	
	
	
	
	
	
	

	Fire Drills - Business
	1 per shift per year
	Periodically
	101-7.2
	
	
	
	
	
	
	


*= If Required

Testing & Inspection Time Defined

	Weekly, or “every 7 days”
	Anytime during a calendar week

	Monthly or “every 30 days”
	Anytime during a calendar month

	Quarterly or “every 3
	3 months from the previous test/inspection,

	months”
	conducted during the 3rd month

	Semi-annually, or “every 6
	6 months from the previous test/inspection,

	months”
	conducted during the 6th month

	Annually or “every 12
	12 months from the previous test/inspection,

	months”
	conducted during the 12th month

	3-Years
	36 months from the previous test/inspection,

	
	conducted during the 36th month

	
	

	5-Years
	60 months from the previous test/inspection,

	
	conducted during the 60th month

	
	

	6-Years
	72 months from the previous test/inspection,

	
	conducted during the 72nd month

	
	




Documentation Should Include the Following:

1. Name of individual performing the activity.

2. Affiliation of the individual performing the activity.

3. The signature of the individual performing the activity.

4. Activity name.

5. Date (month/day/year) that activity was performed.

6. The frequency that is required of the activity.

7. NFPA standard that requires the activity to be performed.

8. The results of the activity, such as “Pass” or “Fail”.

© Copyright 2018 by Keyes Life Safety Compliance, LLC

