POLICY: AIR EXCHANGES, TEMPERATURE, AND HUMIDITY

PURPOSE: An effective ventilation system is in place to minimize airborne microbial contamination. Temperature and humidity control is in place to maintain integrity of sterile packaging.

PROCEDURE: Humidity and Temperature: Room temperature and humidity is checked and recorded every surgery day for the operating rooms. Daily morning checks of temperature and humidity will be recorded by a designated employee. A log sheet will be maintained for each operating room. In the event that the temperature or humidity is outside the acceptable range, the Director of Nursing/Infection Preventionist will be notified immediately for appropriate action.

- Operating room

  - Humidity is maintained between 20 – 60% relative humidity.

    - A relative humidity that is too high can result in damp or moist supplies with added opportunity for fungal growth and other microbial contamination.

    - A relative humidity that is too low can result in excessive dryness, especially in the presence of flammable agents.

  - Room temperature is maintained between 68 – 75 degrees Fahrenheit.

- Clean/sterile storage will have a maximum humidity of 60% and temperature of 72-78 degrees Fahrenheit.

- Air Exchange and Ventilation:

- Doors to the O.R. will remain closed other than during passage of personnel or transportation of instruments and patients.

- Filters are inspected and replaced according to maintenance procedures and manufacturer’s recommendations.

- Primary filtration of 30%.

- Secondary filtration of 90%.

- Operating room air exchanges will be at least 20 per hour.  This will be measured and documented annually by a contracted HVAC service company.

- At least 20% of the total hourly air exchanges should be fresh air.

- Air will enter the O.R. near the ceiling and be removed near the floor.

- Air pressure in the O.R. will be positive relative to the surrounding areas.

- Portable fans and ceiling fans shall not be utilized in any patient treatment areas/rooms.

- Maintenance:

- A trained HVAC service company will perform all preventative and unscheduled maintenance on the ventilation system.

References:

- CDC: Guidelines for Environmental Infection Control in Healthcare Facilities

- Facilities Guidelines Institute